## Questionnaire
Please complete this questionnaire first before proceeding to the second tab "TDH Calc" | [6 empty] | Shape | Circular List | Square List
|  |  |  | Circular | Square/Rectangular |  | Circular | Fiberglass | Concrete
Sewage Ejector & Sump Pump Questionnaire |  |  |  | Fiberglass | Concrete | Fiberglass | Square_Rectangular | Concrete
DATE: |  |  |  | Concrete |  | Concrete
PROJECT NAME:
PROJECT CITY:
PROJECT TYPE:
DESIGNATION (ex. SE-1, SP-2):
VOLTAGE/PHASE: | <Select voltage and phase in cell to left (voltage/phase/Hertz). FOR THE DROPDOWN BUTTON CLICK ON CELL.
SERVICE:
COMPANY:
NAME:
PHONE:
EMAIL:
PUMPS & CONTROLS (to select a choice use the dropdown button for each cell). FOR DROPDOWN BUTTON CLICK ON DESIRED CELL.
PUMP CONFIGURATION: |  |  | PANEL LOCATION:
WATER CLOSET(S)?: |  |  | HCAI/OSHPD CERTIFICATION?:
PUMP TYPE: |  |  | DOOR TYPE:
PUMP LOCATION: |  |  | BACS/BMS INTERFACE:
EXPLOSION-PROOF MOTOR?: |  |  | EMERGENCY POWER?:
GUIDE RAIL/QUICK REMOVAL SYSTEM?: |  |  | CONTROL PANEL MOUNTING:
OPTIONAL: REMOTELY LOCATED ALARM?:
BASIN |  |  | COVER
SHAPE: |  |  | LOAD:
MATERIAL: |  |  | TYPE:
WATER TABLE DEPTH BELOW FINISH GRADE (IF APPLICABLE):
PIPING & VALVES
DISCHARGE OUTLET:
VALVES:
VALVE BOX?: |  | IF YES, SPECIFY MATERIAL:
NOTES:
Note on H18: Tamper Resistant = Exposed Lights
Note on H22: Both options require 120v and wiring back to local control panel
13630 San Antonio Dr.
Norwalk, CA 90650
Phone: 562-364-7430
Fax: 562-474-1327
www.weilaquatronics.com
NEXT >

## TDH Calc
Please complete "Questionnaire" tab first. Please fill out ONLY the yellow highlighted areas | [11 empty] | CIRCULAR Basin Capacities* |  | Circular Lookup Gallons/Foot | Square Basin Gallons/Foot
[10 empty] | Basin Type | Square/Rectangular | Circular Diameter Inches | Gallons/Foot | #VALUE! | 0 | #DIV/0!
DATE: | [9 empty] | Circular |  | 18 | 14 | Run Time Circular Basin | Run Time Square Basin
PROJECT NAME: | 0 | [8 empty] | Square/Rectangular |  | 24 | 24 | #VALUE! | #DIV/0!
PROJECT CITY: | 0 | [10 empty] | 30 | 38
PROJECT TYPE: | 0 | [10 empty] | 36 | 53
DESIGNATION (ex. SE-1, SP-2) | 0 | [10 empty] | 42 | 77
VOLTAGE/PHASE: | 0 | [10 empty] | 48 | 95
SERVICE: | 0 | [10 empty] | 60 | 150
COMPANY: | 0 | [10 empty] | 72 | 212
NAME: | 0 | [10 empty] | 84 | 290
PHONE: | 0 | [10 empty] | 96 | 375
EMAIL: | 0 | [10 empty] | 120 | 587.5
NOTE: INPUT ALL UNITS AS FEET (unless otherwise noted)
INTEGRAL OR DECIMAL NUMBERS ONLY.
VENT TO ROOF
FLOW (IN GPM):
TOTAL HORIZONTAL RUN OF DISCHARGE PIPING (IN FEET):
DISCHARGE
VERTICAL DISTANCE (IN FEET):
FINISHED FLOOR
DEPTH of LOWEST INLET (IN FEET):
[7 empty] | RETENTION DEPTH (IN FEET): | 3
STATIC : |  |  |  |  | MINIMUM WATER
| VERT. DISTANCE FROM F.F. |  | 0 |  | DEPTH (IN FEET): |  | RUN TIME (IN MINUTES): | #DIV/0!
| DEPTH OF LOWEST INLET |  | 0 |  | 1 |  |  | FILL IN FLOW & BASIN INFO FOR FORMULA TO WORK
| RETENTION DEPTH |  | 3
| FLOAT SWITCH ALLOWANCE |  | 1 |  |  |  | BASIN TYPE:
|  |  | 4 | STATIC HEAD
CIRCULAR Basin Diameter
FITTINGS : | [6 empty] | Diameter (IN INCHES)
EQUIVALENT LENGTH of PIPE
PIPE SIZE (IN INCHES): |  |  |  | EQUIVALENT
| FITTINGS: |  | NO. | LENGTH
|  | 90° ELBOW |  | FALSE |  |  | SQUARE/RECTANGULAR Basin Area
|  | 45° ELBOW |  | FALSE |  |  | Length (IN FEET) | Width (IN FEET)
|  | CHECK VALVE | 1 | FALSE | [9 empty] | x
|  | GATE VALVE | 1 | FALSE
|  | TEE |  | FALSE
|  |  |  | 0 |  |  | **Hazen-Williams Coefficient
FRICTION : | [6 empty] | PVC | 150
| 0 | DISCHARGE PIPE Ø (INCHES) |  | C factor**= |  |  | Stainless Steel | 150
| 4 | FEET OF PIPE |  |  |  |  | Copper | 140
| 0 | EQUIVALENT LENGTH OF PIPE (FITTINGS) |  |  |  |  | Ductile Iron | 120
| 4 | TOTAL EQUIVALENT PIPING LENGTH |  |  |  |  | Galv. Iron | 120 | 100
[7 empty] | Cast Iron | 100 | 110
| 4 | FEET OF PIPE |  |  |  |  | Steel | 100 | 120
|  | HEAD LOSS PER 100 FEET OF PIPE | [6 empty] | 130
| 0 | FRICTION | [6 empty] | 140
150
HEAD :
| 4 | STATIC
| 0 | FRICTION
|  | BACK PRESSURE (IF FORCE MAIN) |  |  |  | NOTE: FOR OVERWATCH® INLINE PUMPING SYSTEMS "RETENTION" DEPTH SHALL BE 2 FEET; MINIMUM WATER LEVEL AND ALLOWANCE FOR FLOAT SWITCHES WILL ALL BE ZERO. AFFECTED FIELDS ARE IN GREEN.
| 4 | FEET OF HEAD
BASIN DEPTH: | 0 | DEPTH OF LOWEST INLET
| 3 | RETENTION DEPTH
| 1 | ALLOWANCE FOR FLOAT SWITCHES
| 1 | MINIMUM WATER DEPTH
| 5 | BASIN DEPTH
CALCULATED FLOW VELOCITY: |  | FT/SEC (2.5 FPS MINIMUM TO ACHIEVE PROPER LINE VELOCITY FOR SOLIDS.)
SUMMARY: | 0 | GPM | 4 | FT. TDH | 4 | FT. STATIC
BASIN SIZE: | 0 | DIAMETER (INCHES) | 5 | FT. DEPTH |  | NOTE: STANDBY POWER SOURCE RECOMMENDED FOR OVERWATCH AND OTHER CRITICAL PUMPING SYSTEMS.
Submit forms to eng@weilaquatronics.com
< BACK
13630 San Antonio Dr.
Norwalk, CA 90650
Phone: 562-364-7430
Fax: 562-474-1327
www.weilaquatronics.com
Note on I34: >THREE FEET MINIMUM< (TWO FEET FOR OVERWATCH)
Note on E35: *ZERO FOR OVERWATCH
Note on I36: MUST BE AT LEAST 2 MINUTES.
Note on B37: TO BOTTOM OF PIPE
Note on H43: DIAMETER SUBJECT TO CHANGE DEPENDING ON PUMP SIZE.
Note on C44: CHOOSE PIPE SIZE IN INCHES
Note on F53: CHOOSE COEFFICENT PER PIPING MATERIAL
Note on B75: VELOCITY OVER 8 FT/SEC IS CONSIDERED EXCESSIVE. INCREASE PIPE SIZE OR REDUCE FLOW IF YOUR VELOCITY IS OVER 8 FPS.

## data (hidden)
Pump Configuration
Simplex
Duplex
Triplex
Yes
No
MATERIAL
Fiberglass
Pump Type | Concrete
Submersible
Pneumatic |  | PIPE SIZE
Vertical Column |  | 1.25
1.5
2
Pump location |  | 2.5
Indoor |  | 3
Outdoor |  | 4
6
Door Type |  | 8
Standard |  | 10
Double -Door Deadfront |  | 12
Tamper Resistant
BMS |  | DISCHARGE OUTLET
BACNet |  | Through cover
Other |  | Through side of basin
None
PanelOptions
"Fail-Safe" Alarm (Alerts standby pump loss, high water, or power failure)
High Water Alarm (Alerts high water ONLY)
VALVES
Exposed
Weight |  | Inside valve box
Pedestrian
Vehicle Traffic
Fire Truck
Type |  | VALVE BOX
Grate |  | Fiberglass
Solid (gastight) |  | Concrete
SHAPE
Round
Square